## Panel Schedule Summary
Call Center Building Electrical Panels Summary (Ground Floor)
Panel Name | Load Type | Connected Load (kVA) | Demand Factor (DF) | Demand Load (kVA)
LP-G1 | Normal Lighting | 2.017 | 0.9 | 1.8153
LP-G2 | Normal Lighting | 1.448 | 0.9 | 1.3032
ELP-G1 | Emergency Lighting | 1.186 | 0.9 | 1.0674
ELP-G2 | Emergency Lighting | 1.192 | 0.9 | 1.0728
PP-G | Normal Power (Sockets) | 72 | 0.8 | 57.6
PP-G1 | Normal Power (Sockets) | 47 | 0.8 | 37.6
EPP-G | Emergency Power (Sockets) | 68 | 0.8 | 54.4
HVAC-G1 | Air Conditioning | 74.5 | 0.8 | 59.6
HVAC-G2 | Air Conditioning | 78.375 | 0.8 | 62.7
HVAC-G3 | Air Conditioning | 79.5 | 0.8 | 63.6
Total (1 Floor) | — | 425.218 | — | 340.7587
Total Building (3 Floors) | — | 1275.654 | — | 1022.2761

## 24-Hour Load Profile
Call Center Building Daily Load Summary (3Identical Floor)
Hour | Lighting (kVA) | Power Sockets (kVA) | HVAC (kVA) | Total Hourly Load (kVA) | PF | Total Hourly Load (KW) | load energy curve
00:00 - 01:00 | 1.5776 | 67.32 | 111.54 | 180.4376 | 0.8 | 144.59 | 144.35
01:00 - 02:00 | 1.5776 | 67.32 | 111.54 | 180.4376 | 0.8 | 144.59 | 289.18
02:00 - 03:00 | 1.5776 | 67.32 | 111.54 | 180.4376 | 0.8 | 144.59 | 433.77
03:00 - 04:00 | 1.5776 | 67.32 | 111.54 | 180.4376 | 0.8 | 144.59 | 578.36
04:00 - 05:00 | 1.5776 | 67.32 | 111.54 | 180.4376 | 0.8 | 144.59 | 722.95
05:00 - 06:00 | 3.1552 | 89.76 | 139.425 | 232.3402 | 0.8 | 186.35 | 909.3
06:00 - 07:00 | 9.4657 | 134.64 | 223.08 | 367.1857 | 0.8 | 295.19 | 1204.49
07:00 - 08:00 | 14.1985 | 269.28 | 390.39 | 673.8685 | 0.8 | 541.25 | 1745.74
08:00 - 09:00 | 15.7761 | 403.92 | 501.93 | 921.6261 | 0.8 | 739.7 | 2485.44
09:00 - 10:00 | 15.7761 | 448.8 | 557.7 | 1022.2761 | 0.8 | 820.22 | 3305.66
10:00 - 11:00 | 15.7761 | 448.8 | 557.7 | 1022.2761 | 0.8 | 820.22 | 4125.88
11:00 - 12:00 | 15.7761 | 426.36 | 557.7 | 999.8361 | 0.8 | 802.27 | 4928.15
12:00 - 13:00 | 15.7761 | 403.92 | 557.7 | 977.3961 | 0.8 | 784.32 | 5712.47
13:00 - 14:00 | 15.7761 | 426.36 | 557.7 | 999.8361 | 0.8 | 802.27 | 6514.74
14:00 - 15:00 | 15.7761 | 448.8 | 557.7 | 1022.2761 | 0.8 | 820.22 | 7334.96
15:00 - 16:00 | 15.7761 | 448.8 | 557.7 | 1022.2761 | 0.8 | 820.22 | 8155.18
16:00 - 17:00 | 14.1985 | 359.04 | 501.93 | 875.1685 | 0.8 | 702.29 | 8857.47
17:00 - 18:00 | 11.0433 | 224.4 | 390.39 | 625.8333 | 0.8 | 502.35 | 9359.82
18:00 - 19:00 | 7.888 | 157.08 | 278.85 | 443.8181 | 0.8 | 356.25 | 9716.07
19:00 - 20:00 | 6.3104 | 134.64 | 223.08 | 364.0304 | 0.8 | 292.18 | 10008.25
20:00 - 21:00 | 4.7328 | 112.2 | 167.31 | 284.2428 | 0.8 | 228.11 | 10236.36
21:00 - 22:00 | 3.1552 | 89.76 | 139.425 | 232.3402 | 0.8 | 186.35 | 10422.71
22:00 - 23:00 | 3.1552 | 89.76 | 111.54 | 204.4552 | 0.8 | 164.04 | 10586.75
23:00 - 00:00 | 1.5776 | 67.32 | 111.54 | 180.4376 | 0.8 | 144.59 | 10731.34
Average / Total | 8.8741 | 230.01 | 318.3538 | 13373.7074 |  | 10731.34
MAX Load KW | Energy KW | average load KW | Load factor | cost K
820.22 | 10731.34 | 447.1392 | 0.54515 | 898.2132

## solar gen
Smart Energy Monitoring and Management - Call Center Building (3 Identical Floors)
Hour | Building Load (kW) | Solar Generation (kW) | Self-Consumed Solar (kW) | Net Load / Grid Import (kW) | Solar Share (%) | Grid Dependency (%) | Load Share (%) | Status / Peak
00:00 - 01:00 | 144.59 | 0 | 0 | 144.59 | 0% | 100% | 1.35% | Night Load
01:00 - 02:00 | 144.59 | 0 | 0 | 144.59 | 0% | 100% | 1.35% | Night Load
02:00 - 03:00 | 144.59 | 0 | 0 | 144.59 | 0% | 100% | 1.35% | Night Load
03:00 - 04:00 | 144.59 | 0 | 0 | 144.59 | 0% | 100% | 1.35% | Night Load
04:00 - 05:00 | 144.59 | 0 | 0 | 144.59 | 0% | 100% | 1.35% | Night Load
05:00 - 06:00 | 186.35 | 0 | 0 | 186.35 | 0% | 100% | 1.74% | Night Load
06:00 - 07:00 | 295.19 | 35 | 35 | 260.19 | 11.86% | 88.14% | 2.75% | Day Operation
07:00 - 08:00 | 541.25 | 105 | 105 | 436.25 | 19.4% | 80.6% | 5.04% | Day Operation
08:00 - 09:00 | 739.7 | 210 | 210 | 529.7 | 28.39% | 71.61% | 6.89% | Day Operation
09:00 - 10:00 | 820.22 | 280 | 280 | 540.22 | 34.14% | 65.86% | 7.64% | Day Operation
10:00 - 11:00 | 820.22 | 332.5 | 332.5 | 487.72 | 40.54% | 59.46% | 7.64% | Day Operation
11:00 - 12:00 | 802.27 | 350 | 350 | 452.27 | 43.63% | 56.37% | 7.48% | Day Operation
12:00 - 13:00 | 784.32 | 350 | 350 | 434.32 | 44.62% | 55.38% | 7.31% | Day Operation
13:00 - 14:00 | 802.27 | 332.5 | 332.5 | 469.77 | 41.44% | 58.56% | 7.48% | Day Operation
14:00 - 15:00 | 820.22 | 280 | 280 | 540.22 | 34.14% | 65.86% | 7.64% | Day Operation
15:00 - 16:00 | 820.22 | 210 | 210 | 610.22 | 25.6% | 74.4% | 7.64% | Day Operation
16:00 - 17:00 | 702.29 | 105 | 105 | 597.29 | 14.95% | 85.05% | 6.54% | Day Operation
17:00 - 18:00 | 502.35 | 35 | 35 | 467.35 | 6.97% | 93.03% | 4.68% | Day Operation
18:00 - 19:00 | 356.25 | 0 | 0 | 356.25 | 0% | 100% | 3.32% | Night Load
19:00 - 20:00 | 292.18 | 0 | 0 | 292.18 | 0% | 100% | 2.72% | Night Load
20:00 - 21:00 | 228.11 | 0 | 0 | 228.11 | 0% | 100% | 2.13% | Night Load
21:00 - 22:00 | 186.35 | 0 | 0 | 186.35 | 0% | 100% | 1.74% | Night Load
22:00 - 23:00 | 164.04 | 0 | 0 | 164.04 | 0% | 100% | 1.53% | Night Load
23:00 - 00:00 | 144.59 | 0 | 0 | 144.59 | 0% | 100% | 1.35% | Night Load
Total Energy (kWh/day) | 10731.34 | 2625 | 2625 | 8106.34 | 24.46% | 75.54% | 100% | Daily Totals
MAX Load Grid KW | Energy Grid KW | average load Grid KW | Load factor | cost K
610.22 | 8106.34 | 337.7642 | 0.55351 | 678.5007